Energy M&V Baseline Optimizer

VS Code + Excel — Process Guide

How to prepare data, run the tool, and interpret the Excel output

# 1. What This Tool Does

This tool automates IPMVP Option C measurement and verification analysis. It takes utility billing data for one or more sites, builds weather-normalized regression models to establish an energy baseline, and calculates avoided energy usage and cost savings for a reporting period.

## 1.1 What it analyzes

- Electricity and natural gas consumption — separately, from the same input file

- Multiple sites and meters in a single run

- Sites with multiple concurrent meters — each meter gets its own model, plus a combined aggregated model

- Sites where a meter was replaced — old and new meter data merged into a single timeline

## 1.2 What it produces

- A regression model equation per meter (or per site for aggregated models)

- R² and CV-RMSE quality scores for each model

- Avoided energy usage and cost savings per site for the reporting period

- Meter weight analysis for multi-meter sites (which meters represent what share of load)

- A 12-sheet Excel report with model summaries, bill detail, outlier analysis, and cost tables

## 1.3 Standards compliance

- IPMVP Option C — Whole Building analysis

- ASHRAE Guideline 14 — CV-RMSE threshold of 15% for monthly billing data

- Industry standard R² thresholds: 0.70 for electricity, 0.40 for natural gas

# 2. Prerequisites

## 2.1 Software

You need Python 3.9 or later and the following packages. Install them by opening a terminal and running:

pip install pandas numpy scikit-learn openpyxl

Tkinter (for the file picker dialog) is optional. If unavailable, the tool will ask you to type the file path instead:

pip install tk

## 2.2 Files needed

- The script: download https://github.com/Optimization_M-and-V_public — always use the latest version from the repo

- Your input data: an Excel (.xlsx) file with billing data — see Section 3 for format

# 3. Preparing Your Input Data

## 3.1 File format

The tool accepts an Excel (.xlsx) file. The data can be in one sheet (all service types together) or two separate sheets (one for electricity, one for gas). Column names do not need to match exactly — the interactive column mapping step will connect your column names to what the tool expects.

## 3.2 Required columns

| Column | Required | Description |
| --- | --- | --- |
| Site Name | Yes | Unique identifier for each building or site. All meters for the same building must use the same Site Name. |
| Meter Number | Yes | Utility account or meter ID. Each physical meter should have a unique number. |
| Service Type | Yes | Must contain 'elec' or 'gas' (case-insensitive). Examples: Electricity, Electric, Natural Gas, Gas. |
| Period Start Date | Yes | First day of the billing period. Format: MM/DD/YYYY or YYYY-MM-DD. |
| Period End Date | Yes | Last day of the billing period. |
| HDD | Yes | Heating Degree Days for the billing period. Use a consistent base temperature (typically 65°F) for all rows of the same site. |
| CDD | Yes | Cooling Degree Days for the billing period. |
| Consumption | Yes | Energy usage amount. Standard units: kWh for electricity, Therms for gas. Other units supported — see Section 3.3. |
| Total Charges | Yes | Total dollar amount of the bill. Used to calculate cost savings. |
| Commission Date | Yes* | The date the energy efficiency project was commissioned. Bills before this date = baseline period. Bills on or after = reporting period. Must be the same for all rows of the same site. (*Required if Baseline Bill column is absent.) |
| Baseline Bill | Yes* | Alternative to Commission Date. Value of 1 = baseline bill, 0 = reporting bill. (*Required if Commission Date column is absent.) |
| Consumption Unit | No | Unit of measure for Consumption. Leave blank if data is already in kWh or Therms. See Section 3.3 for supported units. |

## 3.3 Unit conversion

If your consumption data is not in standard units, add a Consumption Unit column and the tool will convert automatically before analysis:

| Service | Units accepted | Converts to |
| --- | --- | --- |
| Electricity | kWh (default), MWh, Wh | kWh |
| Natural Gas | Therms (default), CCF, MCF, MMBTU | Therms |

## 3.4 Minimum data requirements

- Electricity: at least 12 billing rows before the Commission Date per meter

- Natural Gas: at least 8 billing rows before the Commission Date per meter

- Bills must cover all four seasons (at least 1 bill per calendar quarter in the baseline)

- Reporting period: at least 1 bill after the Commission Date to calculate savings (0 reporting bills = model built but no savings calculated)

*Note: Sites with fewer than the minimum baseline bills will not produce a model. The tool will note this in the Quality Dashboard sheet of the output.

## 3.5 Multi-meter sites

If a building has multiple meters, include all meters in the same file. The tool automatically detects whether meters are concurrent (running at the same time) or sequential (one replaced the other):

- Concurrent meters: 2 or more shared billing period start dates. Each meter gets its own model plus an aggregated model summing all meters.

- Sequential meters (meter replacement): non-overlapping billing periods. Treated as a single continuous timeline — one combined model.

# 4. Running the Tool

## 4.1 Interactive mode (recommended)

Open a terminal (PowerShell on Windows, Terminal on Mac), navigate to the folder containing the script from the GitHub repository, and run.

The tool will guide you through the following steps:

Step 1    Select your input file

A file picker dialog will open. Navigate to and select your .xlsx billing data file. If the dialog does not appear (e.g. on a headless server), you will be prompted to type the file path.

Step 2    Sheet detection

The tool detects available sheets in your Excel file:

- Single sheet: automatically used for both electricity and gas (filtered by Service Type)

- Multiple sheets: auto-detected if sheet names contain 'elec' or 'gas'. Otherwise you will be asked to type the sheet name.

Step 3    Column mapping

You will be asked whether you have a saved column mapping configuration from a previous run. If this is your first time:

- Choose 'no'

- The tool shows you the column names in your file

- For each required field, type the corresponding column name from your file (or the letter shown next to it)

- When finished, choose to save the mapping — this creates a .json file you can reuse next time

*Note: Column mapping only needs to be done once per data format. If your billing data always comes in the same column layout, save the mapping and load it on every subsequent run.

Step 4    Analysis runs automatically

No further input needed. The tool processes all sites and meters. Expect approximately 1–3 minutes for a typical portfolio of 10–25 sites. Progress is printed to the terminal.

Step 5    Save the output

A save dialog opens. Choose a location and filename for the results Excel file. The default name includes a timestamp so previous results are not overwritten.

# 5. Understanding the Excel Output

The results file always contains 12 sheets. Every run produces the same sheet structure.

| Sheet | Contents |
| --- | --- |
| Documentation | Metric definitions, quality standards, and interpretation guide |
| Model Summary | One row per model with all key metrics — your primary results table |
| Weather Coverage | HDD and CDD coverage breakdown per model |
| Quality Dashboard | Portfolio-level pass rates and average metric distributions |
| Detailed Site Analysis | Per-site bill tables showing which bills were used, available, or excluded |
| Outlier Analysis | All detected outliers with site, meter, reason, and bill-level detail |
| Electricity Cost Analysis | Avoided cost per electricity meter |
| Gas Cost Analysis | Avoided cost per gas meter |
| Combined Cost Analysis | Site-level savings rollup — use this for reporting totals |
| Meter Weights | Load distribution across meters for concurrent multi-meter sites |
| Original Electricity Data | Your raw input data as loaded |
| Original Gas Data | Your raw input data as loaded |

## 5.1 Model Summary — key columns

| Column | What it means |
| --- | --- |
| Model Type | Individual (single meter) or Aggregated (multi-meter site summed) |
| Model Passes Quality | TRUE if R², CV-RMSE, and Weather Coverage all pass thresholds. This is your primary quality indicator. |
| R2 | How well weather explains consumption variation. Closer to 1.0 is better. Threshold: 0.70 electricity, 0.40 gas. |
| CV-RMSE | Average prediction error as % of mean consumption. Lower is better. Threshold: ≤15%. |
| Weather Coverage (%) | What fraction of the weather range is represented by selected baseline bills. Threshold: ≥75%. |
| Seasonal Strategy | Optimal = at least 2 bills per quarter selected. Acceptable = at least 1 per quarter (fallback). |
| Pct Avoided Usage | % of predicted consumption that was avoided. Positive = savings. Negative = building used more than predicted. |
| Avoided Cost ($) | Dollar value of avoided usage calculated using the measured utility rate. |
| Meter Weight (%) | For concurrent multi-meter sites: this meter's share of total baseline consumption. Empty for single-meter sites. |
| Weight Flag | OK / REVIEW / HIGH RISK based on how much of the site's load comes from failing meters. |
| Coverage Flag | LOW COVERAGE if a passing meter represents less than 25% of site load — its contribution to the aggregate is small. |
| Notes | Automated observations comparing individual vs. aggregated model quality, weight warnings, and sequential meter notes. |

## 5.2 Quality thresholds

| Metric | Electricity | Natural Gas | Standard |
| --- | --- | --- | --- |
| R² | ≥ 0.70 | ≥ 0.40 | Industry standard / ASHRAE Guideline 14 |
| CV-RMSE | ≤ 15% | ≤ 15% | ASHRAE Guideline 14 |
| Weather Coverage | ≥ 75% | ≥ 75% | Hard requirement — IPMVP |
| Min Baseline Bills | 12 | 8 | IPMVP Option C minimum |
| Seasonal Balance | ≥ 2/quarter (preferred) | ≥ 2/quarter (preferred) | IPMVP best practice |

## 5.3 Meter weight flags (multi-meter sites only)

| Flag | Meaning and recommended action |
| --- | --- |
| OK | Failing meters (if any) represent ≤33% of site baseline load. Aggregate model is defensible. |
| REVIEW | Failing meters represent 33–50% of load. Review the aggregate carefully — a meaningful portion of the site's consumption is from meters that could not be individually verified. |
| HIGH RISK | Failing meters represent >50% of load. The aggregate covers more unverified consumption than verified consumption. Consider excluding this site from portfolio savings totals or flagging it explicitly in any reports. |

# 6. Interpreting Results

## What to check first

- Open the Quality Dashboard sheet — this gives you a portfolio-level overview of pass rates, average R², and average CV-RMSE

- Open Model Summary — scan the Model Passes Quality column. Start with any FALSE rows.

- For failing models, look at R², CV-RMSE, and Weather Coverage individually to understand which threshold was missed

- For multi-meter sites, check the Weight Flag column on aggregate rows

- For savings numbers, use the Combined Cost Analysis sheet — it prefers aggregated models for multi-meter sites to avoid double-counting

## 6.2 Common scenarios and what they mean

### Low R² (model fails)

The building's energy consumption is not strongly driven by outdoor temperature. Common causes: significant process or plug loads that don't vary with weather, unusual events during the baseline (shutdown, renovation), or very consistent occupancy that makes consumption flat regardless of season. Models with low R² are still reported — use professional judgment on whether to include them in formal M&V reports.

### High CV-RMSE (model fails)

The model fits some months well and others poorly — the predictions are inconsistent. Often co-occurs with low R². Check for missing or incorrect HDD/CDD values, and verify the baseline period does not span a major operational change.

### Negative % avoided usage

The building used more energy than the baseline model predicts. This is a valid and important finding — it means savings have not been achieved (or were negated by other changes). Negative savings should be reported honestly, not suppressed. Common causes: increased occupancy, new equipment, changes in operating hours, or a baseline that was unusually low.

### 0 reporting bills / 0 avoided cost

The site has a valid baseline model but no reporting period bills in the input data. Either the Commission Date has not yet passed, or the Baseline Bill flag covers the full date range of the file. Once reporting period bills are added, savings will calculate automatically on the next run.

### Several reporting bills excluded as outliers

Reporting bills are excluded when % avoided is below -10% or above +40%. These bounds reflect IPMVP best practice for anomaly detection. If many bills are excluded, investigate the root cause before finalizing the M&V report — an operational change or data issue may have affected the reporting period.

### HIGH RISK weight flag

More than 50% of the site's baseline consumption comes from meters that failed their individual quality check. The aggregate model covers consumption that cannot be individually verified. Depending on your M&V protocol requirements, this site may need to be flagged or excluded from formal savings claims.

# 7. Troubleshooting

| Problem | Likely cause and fix |
| --- | --- |
| File picker does not open | Tkinter is not installed. The tool will prompt for a file path instead — just type the full path to your Excel file. |
| Column mapping validation fails | A required column was not found. Check that the column names you entered match exactly what is in the file (including capitalization and spaces). |
| Site produces no model | Too few baseline bills. Check the minimum requirements in Section 3.4. The Quality Dashboard will list sites that were skipped and why. |
| R² is unexpectedly low (< 0.5) | The building may have significant non-weather-driven load, or the baseline data contains anomalies. Review the Detailed Site Analysis sheet for obvious step-changes or missing months. |
| All savings are 0 | Check that Commission Date or Baseline Bill flags are correctly identifying reporting period bills. If all bills are flagged as baseline, there are no reporting bills to calculate savings from. |
| Output file cannot be saved | The previous output file may be open in Excel. Close it and try again. |
| Tool runs very slowly | Large portfolios with many baseline bills per site can take several minutes. Sites with 20+ baseline bills require testing many combination subsets. This is normal. |
| 'Sequential meter replacement' in Notes | Two meters were merged into a single timeline. Verify this is accurate — if it was a true meter replacement (same load), the combined model is correct. If the meters served different loads, they should not be merged and the input data should be corrected. |

# 8. Quick Reference

## 8.1 Tunable parameters

These constants are defined at the top of the EnergyMVAnalyzer class in the script. Change them to adjust thresholds for your specific project requirements:

| Parameter | Default | Effect of changing |
| --- | --- | --- |
| ELEC_R2_THRESHOLD | 0.70 | Minimum R² for electricity models to pass. Lowering accepts weaker models. |
| GAS_R2_THRESHOLD | 0.40 | Minimum R² for gas models to pass. |
| CVRMSE_THRESHOLD | 15.0 | Maximum CV-RMSE (%) to pass. ASHRAE Guideline 14 standard. |
| WEATHER_COVERAGE_THRESHOLD | 75.0 | Minimum weather coverage (%) for a baseline combination to be tested. |
| ELEC_BASELINE_COUNT | 12 | Number of baseline bills required for electricity. |
| GAS_BASELINE_COUNT | 8 | Number of baseline bills required for gas. |
| WEIGHT_REVIEW_THRESHOLD | 0.33 | Failing meter weight above which aggregate gets a REVIEW flag. |
| WEIGHT_HIGH_RISK_THRESHOLD | 0.50 | Failing meter weight above which aggregate gets a HIGH RISK flag. |
| LOW_COVERAGE_THRESHOLD | 0.25 | Meter weight below which a passing individual meter gets a LOW COVERAGE flag. |
| MAX_COMBINATIONS | 500 | Maximum baseline bill combinations tested per meter. Higher = better optimization but slower. |
| OVERLAP_THRESHOLD | 3 | Shared billing periods required to classify meters as concurrent vs. sequential. |

## 8.2 Output sheet contents at a glance

When looking for specific information, use this guide:

- Did a model pass? → Model Summary → Model Passes Quality

- Why did a model fail? → Model Summary → R2, CV-RMSE, Weather Coverage (%)

- Which bills were used in the model? → Detailed Site Analysis

- Were any bills excluded? → Outlier Analysis

- What are the total savings for a site? → Combined Cost Analysis

- What is the load distribution across meters? → Meter Weights

- What is the portfolio pass rate? → Quality Dashboard